NovaCore X1

Datacenter Cooling System

Technical Specification — Model NCX1-450-RT24

Document Revision 4.2  •  Issued June 15, 2026

# 1. Overview

The NovaCore X1 (model number NCX1-450-RT24) is a precision-controlled, modular datacenter cooling unit designed for high-density server rooms and edge compute facilities. The system delivers a maximum cooling capacity of 450 kilowatts at a reference ambient temperature of 24°C, with a minimum cooling capacity of 80 kilowatts at low-load operation.

The unit is engineered around a closed-loop chilled water heat exchanger and four independent variable-speed compressors. It uses R-1234ze (1,3,3,3-tetrafluoropropene) as the refrigerant, chosen for its global warming potential of less than 1 — substantially below older HFC refrigerants like R-410A.

## 1.1 Intended Use

The NCX1-450-RT24 is intended for indoor installation in datacenters supporting between 200 and 600 kW of IT load. The unit operates between -10°C and 50°C ambient. It is not certified for outdoor or maritime installation.

# 2. System Architecture

The NovaCore X1 is divided into five functional subsystems:

- Refrigeration loop — 4× scroll compressors arranged in two N+1 redundant pairs.

- Chilled water loop — primary heat exchange to the facility's chilled water plant.

- Air handling — 6× EC plug fans, total airflow 28,000 m³/h at nominal load.

- Control and monitoring — embedded ARM Cortex-A53 controller running NovaOS 4.2.

- Filtration — 4 stage progressive filtration (MERV 8 → MERV 13).

## 2.1 Physical Dimensions

| Property | Value |
| --- | --- |
| Height | 2,200 mm (86.6 in) |
| Width | 1,800 mm (70.9 in) |
| Depth | 1,200 mm (47.2 in) |
| Weight (dry) | 1,840 kg (4,057 lb) |
| Weight (operating) | 2,180 kg (4,806 lb) |
| Floor loading | 1,010 kg/m² (207 lb/ft²) |
| Shipping crate volume | 5.8 m³ (205 ft³) |

# 3. Performance Specifications

## 3.1 Cooling Capacity vs Ambient

The following table summarizes derated cooling capacity at varying ambient air temperatures, measured per AHRI Standard 1361.

| Ambient (°C) | Capacity (kW) | EER (kW/kW) | Sensible Heat Ratio |
| --- | --- | --- | --- |
| -10 | 450 | 5.40 | 0.98 |
| 0 | 450 | 5.20 | 0.97 |
| 10 | 450 | 4.95 | 0.96 |
| 20 | 450 | 4.80 | 0.95 |
| 24 | 450 | 4.70 | 0.94 |
| 30 | 430 | 4.45 | 0.93 |
| 35 | 410 | 4.20 | 0.93 |
| 40 | 385 | 3.92 | 0.92 |
| 45 | 352 | 3.60 | 0.91 |
| 50 | 310 | 3.20 | 0.90 |

Note: The reference rating point is 24°C ambient, at which the system delivers exactly 450 kW with an EER of 4.70.

## 3.2 Power Draw

| Load (%) | Compressor Power (kW) | Fan Power (kW) | Total Power (kW) |
| --- | --- | --- | --- |
| 20 | 8.2 | 1.4 | 9.6 |
| 40 | 21.5 | 4.2 | 25.7 |
| 60 | 38.0 | 8.4 | 46.4 |
| 80 | 59.0 | 14.8 | 73.8 |
| 100 | 82.0 | 20.0 | 102.0 |

# 4. Acoustic Performance

Measurements conducted per ISO 3744 in a hemi-anechoic chamber, with the unit mounted on a concrete plinth. Sound power levels are A-weighted (dB(A)).

| Load (%) | Sound Power Lw (dB(A)) | 1m SPL (dB(A)) | 5m SPL (dB(A)) |
| --- | --- | --- | --- |
| 20 | 61 | 53 | 47 |
| 40 | 67 | 59 | 53 |
| 60 | 72 | 64 | 58 |
| 80 | 76 | 68 | 62 |
| 100 | 79 | 71 | 65 |

# 5. Reliability and MTBF

Field-derived mean time between failures (MTBF) by subsystem, based on a population of 1,247 deployed units over 3.7 years of cumulative operation:

| Subsystem | MTBF (hours) | Field Replaceable |
| --- | --- | --- |
| Scroll compressor | 78,000 | Yes (FRU) |
| EC plug fan | 92,000 | Yes (FRU) |
| Refrigeration valve block | 135,000 | No (factory only) |
| NovaOS controller PCB | 215,000 | Yes (FRU) |
| Filtration housing | >500,000 | Yes (FRU) |
| Sensor harness | 180,000 | Yes (FRU) |

# 6. Installation Requirements

## 6.1 Electrical

The unit requires a 3-phase, 480 V AC supply at 60 Hz (or 400 V AC at 50 Hz for international deployments). Total maximum amperage draw at the rated load is 135 amps. A type C-curve 200-amp circuit breaker is recommended.

## 6.2 Refrigerant Loop

The system is factory-charged with 18.5 kg of R-1234ze refrigerant. Field topping is performed using port R-2 on the suction line. Refrigerant work must be conducted by an EPA Section 608 Type II or III certified technician.

## 6.3 Water Supply

The chilled water inlet requires a minimum supply temperature of 7°C and a maximum of 18°C. Required flow rate at peak load is 22 L/s (348 gal/min). The unit ships with a 25 µm strainer that must be cleaned every 4,000 operating hours.

# 7. Maintenance Schedule

| Task | Interval | Estimated Time |
| --- | --- | --- |
| Visual inspection of refrigerant lines | Monthly | 10 minutes |
| Verify chilled water flow rate | Monthly | 5 minutes |
| MERV 8 prefilter replacement | Every 1,500 operating hours | 20 minutes |
| MERV 13 filter replacement | Every 2,500 operating hours | 30 minutes |
| Chilled water strainer cleaning | Every 4,000 operating hours | 45 minutes |
| Compressor oil sampling | Annually | 60 minutes |
| Refrigerant leak detection (electronic) | Annually | 30 minutes |
| Full system pressure test and recalibration | Every 5 years | 4 hours |

Note: Filter changes occur every 2,500 operating hours for the MERV 13 stage. The MERV 8 prefilter, which extends MERV 13 life, is changed every 1,500 operating hours.

# 8. Standards and Compliance

The NovaCore X1 is certified to or compliant with the following standards:

- ASHRAE Standard 90.4 — Energy Standard for Data Centers

- ASHRAE Standard 62.1 — Ventilation for Acceptable Indoor Air Quality

- AHRI Standard 1361 — Performance Rating of Computer Room and Data Center Cooling Units

- EU EcoDesign Regulation 2021/341

- UL 1995 / CSA C22.2 No. 236 — Heating and Cooling Equipment

- RoHS Directive 2011/65/EU

- REACH Regulation (EC) No 1907/2006

## 8.1 Refrigerant Compliance

R-1234ze has a global warming potential (GWP) of less than 1 (specifically 0.97 over a 100-year horizon per IPCC AR5). This places the NovaCore X1 firmly under EU F-Gas Regulation (517/2014) thresholds, with no phase-down obligations through 2050.

# 9. Warranty

NovaCore Industries warrants the NCX1-450-RT24 against defects in material and workmanship for a period of 60 months from the date of factory shipment, or 50,000 operating hours, whichever occurs first.

## 9.1 Extended Coverage

Optional extended coverage can be purchased that extends warranty to 96 months or 80,000 hours. The extended plan includes annual on-site preventive maintenance visits and prioritized field service response within 4 hours during business days.

# 10. Support and Contacts

| Region | Phone | Email |
| --- | --- | --- |
| North America (Atlanta) | +1 (404) 555-0182 | support-na@novacore.example |
| Europe (Amsterdam) | +31 20 555 0192 | support-eu@novacore.example |
| Asia-Pacific (Singapore) | +65 6555 0114 | support-apac@novacore.example |
| Emergency 24/7 (Global) | +1 (800) 555-0167 | ops@novacore.example |

Document control: this specification (Rev 4.2) supersedes Rev 4.1 issued December 2025. The next scheduled revision is December 2026.